## Slide 1: 50 mega Watt (AC) Solar farm – 350 Acres - Alpine, Texas. Energy Harvest for the City of Houston. View looking ESE Solairedirect / Engie Solar – developer of the project

## Slide 2: The Trackers were designed by NexTracker.com, the dominant tracker manufacturer

## Slide 3: 315 watt solar panel –197,000 Panels Note that the were made in Turkey.

## Slide 4: Mechanism to tilt 80 panels – 25.2 k Watts; 40 to left,40 to right 1. Small panel on the left provides power for tilt motor – 30 watts. 2. Worm gearbox is being driven by a small DC motor. – The duty cycle is intermittent. 3. Wifi antenna (top, partially visible) - communication. 4. The bent tube allows the center of gravity of the array to be located on the axis of rotation.

## Slide 5: Early morning deployment. Max tilt angle is so one row does not shade the next row.

## Slide 6: Looking west – with 2 mega watt inverter from Kaco in San Antonio – 1 of 26. Now the inverters are 3 Mega watt each.

## Slide 7: Shock absorber to dampen out any wind induced vibrations. I noted that the natural frequency of vibration of the beam was 2 cycles per second. Rule of thumb, 2 cycles or higher to avoid flutter.

## Slide 8: Intermediate support. The 5” EMT horizontal tube supports the panels. The columns are driven into the soil (30 seconds -typical drive time), using GPS to locate them. The brackets shown, allow slight adjustment, in 3 dimensions.

## Slide 9: Google: Local Sun Energy in Sealy, Tx Destruction due to a microburst – late May,2017

## Slide 10: Array – 32’ x 81’ before a high wind event. The wind flipped the some panels off of the structure as a monolith. The panels were together, as well as tied to the wooden frame. There may have been thermal cycling, weakening the fasteners.